## Grnding
Client |  | Southerland Assoc
Project |  | Osmose Rock Hill
Project No
CSC Provided and Installed Grounding System | Buried Wire Ft | Size | Grd Rods, 3/4 in X 10 Ft | Conn Wire Ft | Size | RGS Conduit Ft | size | Provide all hardware, cadwels and parts to complete
MEA Storage Tk 1 | 260 | #4/0 | 2 | 70 | #4/0 | 60 | 1 | Bury 24 in below grade around dike
MEA Storage Tk 2 |  |  |  | 70 | #4/0 | 60 | 1
MEA Storage Tk 3 |  |  |  | 70 | #4/0 | 60 | 1
MEA Storage pmp mtr 1 |  |  |  | 70 | #4/0 | 60 | 1
MEA Storage pmp mtr 2 |  |  |  | 70 | #4/0 | 60 | 1
MEA Storage pmp mtr 3 |  |  |  | 70 | #4/0 | 60 | 1
CCA Proc Wtr Pump mtr | 40 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grd ring below grade
Pre-Coat Tank | 60 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grd ring below grade
Pre-Coat Tank agitator |  |  |  | 15 | #4/0 | 10 | 1
Filter Feed Tk pmp mtr |  |  |  | 15 | #4/0 | 10 | 1
Finished Product Filter |  |  |  | 15 | #4/0 | 10 | 1
CCA Storage Tank-1 | 80 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grnd grid buried below grade
CCA Storage Tank-1 |  |  |  | 15 | #4/0 | 10 | 1
CCA loadout pmp mtr |  |  |  | 15 | #4/0 | 10 | 1
QUAT Pmp mtr |  |  |  | 15 | #4/0 | 10 | 1
NW100 A Tanks | 100 | #4/0 |  | 15 | #4/0 | 10 | 1 | Bury 24 in below grade around dike
NW100 B Tanks |  |  |  | 15 | #4/0 | 10 | 1
New Reactor | 100 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grnd grid buried below grade
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
New Reactor equipment & mtr |  |  |  | 15 | #4/0 | 10 | 1
100 HP Blower | 40 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grd ring
Boilerhouse | 150 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grd ring
CO2 Tank Farm | 100 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grd ring
Cooling Tower | 100 | #4/0 |  | 15 | #4/0 | 10 | 1 | Attach to existing grd ring
Subtotals | 640 | #4/0 |  | 780 | #4/0 | 600 | 1" rigid conduit
[10 empty] | Cost | sell | MH Ea | Unit MH | Labor Sell
Total | 520 | Ft 1" rigid conduit | [6 empty] | per 100 ft | 55 | 286 | 1 | 5.2 | 236.34
Total | 1420 | Ft #4/0 Bare Copper | [6 empty] | per 100 ft | 22 | 312.4 | 1 | 14.2 | 645.39
Total | 2 | Ground Rods | [6 empty] | each | 20 | 0.4 | 4 | 8 | 363.6
Total | 35 | Conduit runs and hardware | [6 empty] | each | 25 | 875 | 1.5 | 52.5 | 2386.125
[9 empty] | Totals |  | 1473.8 |  | 79.9 | 3631.455

## Heat Trace
Client |  | Southerland Assoc
Project |  | Osmose Rock Hill
Project No
CSC Provided and installed | QUAT Tank | MEA Stor Tk | NW PW Stor Tk | totals
[7 empty] | Cost | Sell unit | MH Ea | Unit MH | Labor Sell
Pwr Conn Box | 2 | 1 | 2 | 5 |  |  | 36.53 | 219.18 | 0.5 | 2.5 | 113.625
Thermostats-NEMA 4, 0-200F, Pipe Mtd w/Cap bulb 72" AFF at Gnd | 2 | 1 | 2 | 5 |  |  | 146.66 | 879.96 | 1 | 5 | 227.25
End of Circuit Pwr-on Ind. Mtd in NEMA 4 encl | 2 | 1 | 2 | 5 |  |  | 62.15 | 372.9 | 1 | 5 | 227.25
Pipe Straps | 4 | 2 | 4 | 10 |  |  | 2.11 | 25.32 | 0.3 | 3 | 136.35
20A SP 277vac GFCI Ckt Bkrs | 2 | 1 | 2 | 5 |  |  |  | 0 | 0.5 | 2.5 | 113.625
Wattage of HT Cable | 3 | 1 | 1 | [7 empty] | 0
Feet Of HT Cable, 277vac | 240 | 120 | 320 | 240 | Ft 3 watt |  | 2.23 | 642.24 | 3 | 7.2 | 327.24
|  |  |  | 440 | Ft 1 watt |  | 2.23 | 1177.44 | 3 | 13.2 | 599.94
[6 empty] | Material cost |  | 3317.04 |  | 38.4 | 1745.28

## Ctr&Pwr
| Client |  | Southerland Assoc
| Project |  | Osmose Rock Hill |  | This page is copied into the formal proposal
| Project No |  | NW 100 Electrical |  | Material shown is used on the yellow pages
| Conditional notes | 1. | All areas are to be considered non-hazardous general purpose
|  | 2. | Two men are included for two week checkout and startup
|  | 3. | All motor disconnects switches are HP rated and NEMA 3R type.
|  | 4. | Conduit shall be Galvanized rigid outside and EMT inside Buildings
|  | 5. | Wiring will be copper with THHN insulation 14 gauge and larger and TFFN 16 Gauge and smaller
|  | 6. | Control cable (120 volt) will be #16 ether single or twisted pair with no shield.
|  | 7. | Instrument cable (24 volt) will be 2C (two conductor) #16 copper twisted shielded pair Beldon #8760 or equal in conduit.
|  | 8. | All devices will be provided by owner except as listed below as CSC provided. CSC will mount instruments not installed in-line by mechanical contractor as shown in Scope of Work listed below.
|  | 9. | Local motor start/stop pushbutton stations will be NEMA 4 with covered "STOP" button and provided as listed.
|  | 10. | Air operated valves will be tubed by CSC with 3 ft of 1/4" copper as listed.
|  | 11. | PLC Panel (3 ft X 6 ft) will be mounted to block wall by CSC. Location to be outside control room near new reactor.
|  | 12. | OWS (Operator Workstation) will be freestanding and set outside tank dike near existing water pump.
|  | 13. | NO tray is included in this proposal, if required design must be submitted and pricing adjusted as necessary.
|  | 14. | NO emergency/code lighting has been included except for the relocation of one existing exit sign.
|  | 15. | All conduit will be home run as CSC sees fit since no routing plans have been submitted. Conduit that that begins inside the building and runs to outside equipment will be EMT inside and Rigid outside the building.
|  | 16. | Proposal does NOT include obtaining any permits or licenses required for the installation
|  | 17. | NO junction boxes of any kind are included in the proposal. Primary conduit runs will be teed off directly to instrument or device and terminated at device with a 2 foot section of waterproof flexible conduit.
|  | 18. | All wire terminations will be marked with a wire number using the terminating field device ID unless otherwise instructed.
|  | 19. | Wiring of safety shower heaters are not included in proposal
|  | 20. | Any additions or changes to the scope of work as listed will require an approved change order and may impact schedule.
| Tag | HP | CSC Provided | Scope of Work | from | to | cond ft | size | Type | cable ft | type | cond ft | size | type | ID | qty
| PLC-1 |  |  | Mt on wall near reactor | ER | PLC | 100 | 0.75 | emt | 120 | 3C#12 THHN |  |  |  | P-4 | 1
| OWS-1 |  |  | Set near wtr pmp | ER | OWS | 100 | 0.75 | emt | 110 | 3C#12 THHN |  |  |  | P-5 | 1
| OWS-1 |  |  | Set near wtr pmp | PLC | OWS | 50 | 0.75 | emi | 220 | coax RG59/U |  |  |  | N-1 | 1
| LT-CCA20 |  |  | con&wire | CCA Tk | PLC | 20 | 0.75 | rgs | 130 | 2C#16 shd | 100 | 1 | rgs | C-1 | 4
| LT-CCA26 |  |  | con&wire | CCA Tk | PLC | 20 | 0.75 | rgs | 130 | 2C#16 shd |  |  |  | C-1
| LT-QUAT |  |  | con&wire | QUAT Tk | PLC | 20 | 0.75 | rgs | 130 | 2C#16 shd |  |  |  | C-1
| FT-QUAT |  |  | con&wire | QUAT PMP | PLC | 20 | 0.75 | rgs | 130 | 2C#16 shd |  |  |  | C-1
| FV-CCA20-1 |  |  | con, wire & 3 ft tubing | CCA Tk | PLC | 20 | 1 | rgs | 700 | 2C#16 | 200 | 2.5 | rgs | C-2 | 21
| FV-CCA-20-2 |  |  | con, wire & 3 ft tubing | CCA Tk | PLC | 20 | 1 | rgs | 700 | 2C#16 |  |  |  | C-2
| FV-CCA26-1 |  |  | con, wire & 3 ft tubing | CCA Tk | PLC | 20 | 1 | rgs | 700 | 2C#16 |  |  |  | C-2
| FV-CCA26-2 |  |  | con, wire & 3 ft tubing | CCA Tk | PLC | 20 | 1 | rgs | 700 | 2C#16 |  |  |  | C-2
| FV-QUAT-1 |  |  | con, wire & 3 ft tubing | QUAT Tk | PLC | 20 | 1 | rgs | 700 | 2C#16 |  |  |  | C-2
| FV-QUAT-2 |  |  | con, wire & 3 ft tubing | QUAT Tk | PLC | 20 | 1 | rgs | 700 | 2C#16 |  |  |  | C-2
| FV-QUAT-3 |  |  | con, wire & 3 ft tubing | QUAT Pmp | PLC | 20 | 1 | rgs | 700 | 2C#16 |  |  |  | C-2
| HS-CCA-M15 |  | LDS, PB-Sta | Mtd, Con&wire | CCA Pmp | PLC | 20 | 0.75 | rgs | 260 | 2C#16 | 100 | 1 | rgs | C-3 | 7
| HS-QUAT-M2 |  | LDS, PB-Sta | Mtd, Con&wire | CCA Pmp | PLC | 20 | 0.75 | rgs | 260 | 2C#16 |  |  |  | C-3
| VS-QUAT |  |  | con&wire | MCC | PLC | 100 | 0.75 | rgs | 110 | 2C#16 shd |  |  |  | C-3
| LT-NW100-A |  |  | con&wire | Tank | PLC | 20 | 0.75 | rgs | 180 | 2C#16 shd | 150 | 1.25 | rgs | C-4 | 6
| LT-NW100-B |  |  | con&wire | Tank | PLC | 20 | 0.75 | rgs | 180 | 2C#16 shd |  |  |  | C-4
| LT-NW100-C |  |  | con&wire | Tank | PLC | 20 | 0.75 | rgs | 180 | 2C#16 shd |  |  |  | C-4
| LT-NW100-D |  |  | con&wire | Tank | PLC | 20 | 0.75 | rgs | 180 | 2C#16 shd |  |  |  | C-4
| LT-NW100-E |  |  | con&wire | Tank | PLC | 20 | 0.75 | rgs | 180 | 2C#16 shd |  |  |  | C-4
| WE-NW100-S |  |  | con&wire | Tank | PLC | 20 | 0.75 | rgs | 180 | 2C#16 shd |  |  |  | C-4
| FV-NW100-A-1 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 | 150 | 2 | rgs | C-5 | 18
| FV-NW100-A-2 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-5
| FV-NW100-B-1 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-5
| FV-NW100-B-2 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-5
| FV-NW100-C-1 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-5
| FV-NW100-C-2 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-5
| FV-NW100-D-1 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 | 150 | 2 | rgs | C-6 | 12
| FV-NW100-D-2 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-6
| FV-NW100-E-1 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-6
| FV-NW100-E-2 |  |  | con, wire & 3 ft tubing | Tank | PLC | 20 | 1 | rgs | 510 | 2C#16 |  |  |  | C-6
| HS-MW100-TP |  | LDS, PB-Sta | Mtd, Con&wire | Trans Pmp | PLC | 20 | 0.75 | rgs | 260 | 2C#16 | 100 | 1 | rgs | C-7 | 4
| HS-MW100-LP |  | LDS, PB-Sta | Mtd, Con&wire | Ldout Pmp | PLC | 20 | 0.75 | rgs | 260 | 2C#16 |  |  |  | C-7
| KV-Bag UnL |  |  | con&wire | Bag Unl | PLC | 20 | 0.75 | rgs | 270 | 2C#16 | 60 | 2 | EMT | C-8 | 15
| FV-R1 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-8
| FV-R2 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-8
| FV-R3 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-8
| FV-R4 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-8
| FV-R5 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 | 60 | 2 | EMT | C-9 | 16
| FV-R6 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-9
| FV-R7 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-9
| FV-R8 |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-9
| FV-AF |  |  | con, wire & 3 ft tubing | Reac | PLC | 20 | 0.75 | rgs | 270 | 2C#16 |  |  |  | C-9
| LS-REAC |  |  | con&wire | Reac | PLC | 20 | 0.75 | rgs | 90 | 2C#16 |  |  |  | C-9
| FCV-R1 |  |  | con, wire & 3 ft tubing | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd | 60 | 1.25 | EMT | C-10 | 7
| TCV-R2 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd |  |  |  | C-10
| TCV-R3 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd |  |  |  | C-10
| FT-R1 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd |  |  |  | C-10
| FT-R2 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd |  |  |  | C-10
| FT-R3 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd |  |  |  | C-10
| LT-REAC |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 2C#16 shd |  |  |  | C-10
| TE-REAC |  |  | con&wire | Reac | PLC | 20 | 0.75 | emt | 90 | 3C#16 shd | 60 | 1 | emt | C-11 | 2
| TE-HEATEXC |  |  | con&wire | Reac | PLC | 20 | 0.75 | emt | 90 | 3C#16 shd |  |  |  | C-11
| FT-R1 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 3C#16 | 60 | 1 | EMT | P-1
| FT-R2 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 3C#16 |  |  |  | P-1
| FT-R3 |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 3C#16 |  |  |  | P-1
| LT-REAC |  |  | con&wire | REAC | PLC | 20 | 0.75 | emt | 90 | 3C#16 |  |  |  | P-1
| HS-CT FAN |  | LDS, PB-Sta | Mtd, Con&wire | CT Fan | PLC | 20 | 0.75 | EMT | 190 | 2C#16 | 60 | 1.5 | EMT | C-12 | 12
| HS CT PMP |  | LDS, PB-Sta | Mtd, Con&wire | CT Pmp | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-12
| HS-AF MIXER |  | LDS, PB-Sta | Mtd, Con&wire | AF-Mixer | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-12
| HS-AF-PMP |  | LDS, PB-Sta | Mtd, Con&wire | AF-Pmp | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-12
| HS-BAG RV |  | LDS, PB-Sta | Mtd, Con&wire | Bag Unl | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-12
| HS-R MIXER |  | LDS, PB-Sta | Mtd, Con&wire | Reac Mixer | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-12
| HS-R VAC PMP |  | LDS, PB-Sta | Mtd, Con&wire | Reac VP | PLC | 20 | 0.75 | EMT | 190 | 2C#16 | 60 | 1.5 | EMT | C-13 | 10
| HS-R RV |  | LDS, PB-Sta | Mtd, Con&wire | Reac FR RV | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-13
| HS-R PMP |  | LDS, PB-Sta | Mtd, Con&wire | Reac Pmp | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-13
| HS-R-PD BL |  | LDS, PB-Sta | Mtd, Con&wire | Reac PDB | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-13
| HS-CO BAG RV |  | LDS, PB-Sta | Mtd, Con&wire | CO Bag Unl | PLC | 20 | 0.75 | EMT | 190 | 2C#16 |  |  |  | C-13
| FV-MEA-1-1 |  |  | con, wire & 3 ft tubing | mea Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 | 300 | 2 | rgs | C-14 | 18
| FV-MEA-1-2 |  |  | con, wire & 3 ft tubing | mea Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-14
| FV-MEA-1-3 |  |  | con, wire & 3 ft tubing | mea Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-14
| FV-MEA-2-4 |  |  | con, wire & 3 ft tubing | mea Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-14
| FV-MEA-2-5 |  |  | con, wire & 3 ft tubing | mea Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-14
| FV-MEA-2-6 |  |  | con, wire & 3 ft tubing | mea Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-14
| FV-P/ST-7 |  |  | con, wire & 3 ft tubing | P/S Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 | 300 | 2 | rgs | C-15 | 16
| FV-P/ST-8 |  |  | con, wire & 3 ft tubing | P/S Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-15
| FV-P/ST-9 |  |  | con, wire & 3 ft tubing | P/S Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-15
| FV-P/ST-10 |  |  | con, wire & 3 ft tubing | P/S Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-15
| FV-P/ST-11 |  |  | con, wire & 3 ft tubing | P/S Tk | PLC | 20 | 0.75 | rgs | 990 | 2C#16 |  |  |  | C-15
| LT-P/ST-1 |  |  | con&wire | P/S Tk | PLC | 20 | 0.75 | rgs | 280 | 2C#16 shd | 250 | 1.25 | rgs | C-16 | 5
| LT-MEA-1-2 |  |  | con&wire | MEA Tk | PLC | 20 | 0.75 | rgs | 280 | 2C#16 shd |  |  |  | C-16
| LT-MEA-2-3 |  |  | con&wire | MEA Tk | PLC | 20 | 0.75 | rgs | 280 | 2C#16 shd |  |  |  | C-16
| FT-P/ST PW |  |  | con&wire | P/S Tk | PLC | 20 | 0.75 | rgs | 280 | 2C#16 shd |  |  |  | C-16
| FT-MEA-PMP |  |  | con&wire | MEA Pmp | PLC | 20 | 0.75 | rgs | 280 | 2C#16 shd |  |  |  | C-16
| TE-P/ST |  |  | con&wire | P/S Tk | PLC | 20 | 0.75 | rgs | 280 | 3C#16 shd | 250 | 0.75 | rgs | C-17 | 1
| FT-P/ST PW |  |  | con&wire | P/S Tk | PLC | 20 | 0.75 | rgs | 280 | 3C#16 | 250 | 1 | rgs | P-2 | 2
| FT-MEA-PMP |  |  | con&wire | MEA Pmp | PLC | 20 | 0.75 | rgs | 280 | 3C#16 |  |  |  | P-2
| HS-P/SPMP |  | LDS, PB-Sta | Mtd, Con&wire | p/s Pmp | PLC | 20 | 0.75 | rgs | 550 | 2C#16 | 250 | 1.5 | rgs | C-18 | 8
| HS-MEA PMP |  | LDS, PB-Sta | Mtd, Con&wire | MEA Pmp | PLC | 20 | 0.75 | rgs | 550 | 2C#16 |  |  |  | C-18
| HS-MEA SP-1 |  | LDS, PB-Sta | Mtd, Con&wire | MEA Sump-1 | PLC | 20 | 0.75 | rgs | 550 | 2C#16 |  |  |  | C-18
| HS-MEA-SP-2 |  | LDS, PB-Sta | Mtd, Con&wire | MEA-Sump-2 | PLC | 20 | 0.75 | rgs | 550 | 2C#16 |  |  |  | C-18
| LT-FF TK |  |  | con&wire | FP Filter | PLC | 20 | 0.75 | EMT | 110 | 2C#16 | 80 | 0.75 | emt | C-19 | 2
| FT-FP-FILT |  |  | con&wire | FP Filter | PLC | 20 | 0.75 | EMT | 110 | 2C#16 |  |  |  | C-19
| FT-FP-FILT |  |  | con&wire | FP Filter | PLC | 20 | 0.75 | emt | 110 | 3C#16 | 100 | 0.75 | emt | P-3 | 1
| HS-FF TK PMP |  | LDS, PB-Sta | Mtd, Con&wire | FF-Tk Pmp | PLC | 20 | 0.75 | EMT | 220 | 2C#16 | 80 | 1.25 | emt | C-18 | 6
| HS-PC-AG |  | LDS, PB-Sta | Mtd, Con&wire | Precoat Ag | PLC | 20 | 0.75 | EMT | 220 | 2C#16 |  |  |  | C-18
| HS-FF-AG |  | LDS, PB-Sta | Mtd, Con&wire | FF Agit | PLC | 20 | 0.75 | EMT | 220 | 2C#16 |  |  |  | C-18
| HS-NW100 PWP |  | LDS, PB-Sta | Mtd, Con&wire | PUMP | PLC | 20 | 0.75 | EMT | 300 | 2C#16 | 120 | 1 | rgs | C-19 | 6
| HS-CCA-PWP |  | LDS, PB-Sta | Mtd, Con&wire | PUMP | PLC | 20 | 0.75 | EMT | 300 | 2C#16 |  |  |  | C-19
| MCC-1 |  | 6 SECTION | inst, con&wire
| LF-1 |  | 277vac Fl Fix in warehouse | inst, con&wire |  |  | 30 | 0.75 | emt | 110 | 1C#10
| LF-2 |  | 277vac Fl Fix in warehouse | inst, con&wire |  |  | 30 | 0.75 | emt | 110 | 1C#10
| LF-existing-1 |  | Move | Re-install & wire |  |  | 30 | 0.75 | emt | 110 | 1C#10
| LF-existing-2 |  | Move | Re-install & wire |  |  | 30 | 0.75 | emt | 110 | 1C#10
| CktBrk-600AMP |  | Instal in Ex. MDP in ER | inst, con&wire | MDP | MCC |  |  |  | 120 | 350MCM | 30 | 3 | rgs | C-20 | 3
| (see Above) |  | Instal in Ex. MDP in ER | inst, con&wire | MDP | MCC |  |  |  | 120 | 350MCM | 60 | 3 | rgs | C-21 | 3
1 | CCA LO Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 | 80 | 2 | emt | C-22 | 24
2 | QUAT Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
3 | MW100 T Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
4 | MW100 LO Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
5 | CT Fan |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
6 | CT Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
7 | AF Tk Mix |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
8 | AF-Add Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
9 | Bag UnL RV |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
10 | Reac Mixer |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
11 | Reac Vac Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
12 | Rac FR RV |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
13 | Reac Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
14 | Reac PD Blower |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
15 | CO Bag UnL |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
16 | PreHt Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
17 | MEA Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
18 | MEA Sump 1 |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
19 | MEA Sump 2 |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
20 | MW100 PW Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
21 | CCA PW Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
22 | FF Tk Pmp |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
23 | Pre-Coat Agit |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
24 | FF Tk Agit |  |  | Con&wire | MCC | PLC |  |  |  | 100 | 2C#16 |  |  |  | C-22
C-22
1 | CCA LO Pmp | 15 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 400 | 1C#8, | 120 | 0.75 | rgs | P-6 | 4
1 | CCA LO Pmp |  |  |  | MTR | MCC |  |  |  | 130 | 1C#10 |  |  |  | P-6
2 | QUAT Pmp | 2 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 400 | 1C#8, | 120 | 0.75 | rgs | P-7 | 4
2 | QUAT Pmp |  |  |  | MTR | MCC |  |  |  | 130 | 1C#10 |  |  |  | P-7
3 | MW100 T Pmp | 15 | Non-fused Disc | Ckt Exist ad switch | MTR | MCC
4 | MW100 LO Pmp | 15 | Non-fused Disc | Ckt Exist ad switch | MTR | MCC
5 | CT Fan | 10 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 290 | 1C#10 | 80 | 0.75 | rgs | P-8 | 4
5 | CT Fan |  |  |  | MTR | MCC |  |  |  | 90 | 1C#12 |  |  |  | P-8
6 | CT Pmp | 10 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 930 | 1C#10 | 300 | 0.75 | rgs | P-9 | 4
6 | CT Pmp |  |  |  | MTR | MCC |  |  |  | 310 | 1C#12 |  |  |  | P-9
7 | AF Tk Mix | 1.5 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 290 | 1C#10 | 80 | 0.75 | emt | P-10 | 4
7 | AF Tk Mix |  |  |  | MTR | MCC |  |  |  | 90 | 1C#12 |  |  |  | P-10
8 | AF-Add Pmp | 1.5 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 290 | 1C#10 | 80 | 0.75 | emt | P-11 | 4
8 | AF-Add Pmp |  |  |  | MTR | MCC |  |  |  | 90 | 1C#12 |  |  |  | P-11
9 | Bag UnL RV | 1 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 460 | 1C#10 | 150 | 0.75 | emt | P-12 | 4
9 | Bag UnL RV |  |  |  | MTR | MCC |  |  |  | 160 | 1C#12 |  |  |  | P-12
10 | Reac Mixer | 15 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 460 | 1C#8 | 150 | 0.75 | emt | P-13 | 4
10 | Reac Mixer |  |  |  | MTR | MCC |  |  |  | 160 | 1C#10 |  |  |  | P-13
11 | Reac Vac Pmp | 15 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 460 | 1C#8 | 150 | 0.75 | emt | P-14 | 4
11 | Reac Vac Pmp |  |  |  | MTR | MCC |  |  |  | 160 | 1C#10 |  |  |  | P-14
12 | Rac FR RV | 1 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 460 | 1C#10 | 150 | 0.75 | emt | P-15 | 4
12 | Rac FR RV |  |  |  | MTR | MCC |  |  |  | 160 | 1C#12 |  |  |  | P-15
13 | Reac Pmp | 15 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 460 | 1C#10 | 150 | 0.75 | emt | P-16 | 4
13 | Reac Pmp |  |  |  | MTR | MCC |  |  |  | 160 | 1C#12 |  |  |  | P-16
14 | Reac PD Blower | 100 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 460 | 1C#2/0 | 150 | 2 | emt | P-17 | 4
14 | Reac PD Blower |  |  |  | MTR | MCC |  |  |  | 160 | 1C#4 |  |  |  | P-17
15 | CO Bag UnL | 1 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 290 | 1C#8 | 80 | 0.75 | emt | P-18 | 4
15 | CO Bag UnL |  |  |  | MTR | MCC |  |  |  | 90 | 1C#10 |  |  |  | P-18
16 | PreHt Pmp | 10 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 550 | 1C#8 | 180 | 0.75 | rgs | P-19 | 4
16 | PreHt Pmp |  |  |  | MTR | MCC |  |  |  | 190 | 1C#10 |  |  |  | P-19
17 | MEA Pmp | 10 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 550 | 1C#8 | 180 | 0.75 | rgs | P-20 | 4
17 | MEA Pmp |  |  |  | MTR | MCC |  |  |  | 190 | 1C#10 |  |  |  | P-20
18 | MEA Sump 1 | 1 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 550 | 1C#8 | 180 | 0.75 | rgs | P-21 | 4
18 | MEA Sump 1 |  |  |  | MTR | MCC |  |  |  | 190 | 1C#10 |  |  |  | P-21
19 | MEA Sump 2 | 1 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 550 | 1C#8 | 180 | 0.75 | rgs | P-22 | 4
19 | MEA Sump 2 |  |  |  | MTR | MCC |  |  |  | 190 | 1C#10 |  |  |  | P-22
20 | MW100 PW Pmp | 5 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 550 | 1C#8 | 180 | 0.75 | rgs | P-23 | 4
20 | MW100 PW Pmp |  |  |  | MTR | MCC |  |  |  | 190 | 1C#10 |  |  |  | P-23
21 | CCA PW Pmp | 5 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 350 | 1C#8 | 100 | 0.75 | rgs | P-24 | 4
21 | CCA PW Pmp |  |  |  | MTR | MCC |  |  |  | 110 | 1C#10 |  |  |  | P-24
22 | FF Tk Pmp | 20 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 350 | 1C#8 | 100 | 0.75 | rgs | P-25 | 4
22 | FF Tk Pmp |  |  |  | MTR | MCC |  |  |  | 110 | 1C#10 |  |  |  | P-25
23 | Pre-Coat Agit | 0.5 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 350 | 1C#8 | 100 | 0.75 | emt | P-26 | 4
23 | Pre-Coat Agit |  |  |  | MTR | MCC |  |  |  | 110 | 1C#10 |  |  |  | P-26
24 | FF Tk Agit | 3 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 350 | 1C#8 | 100 | 0.75 | emt | P-27 | 4
24 | FF Tk Agit |  |  |  | MTR | MCC |  |  |  | 110 | 1C#10 |  |  |  | P-27
25 | Exh Fan | 2 | Non-fused Disc | Inst, Cond & Wire | MTR | MCC |  |  |  | 400 | 1C#10 | 125 | 0.75 | emt | P-41 | 4
25 | Exh Fan | [8 empty] | 135 | 1C#12 |  |  |  | P-41 | 4
HT | QUAT Heat Trace |  | See Heat Trace | Inst, Cond & wire | Ex LPI Pnl | Quat Tk |  |  |  | 130 | 1C #10 | 30 | 0.75 | rgs | P-28 | 3
HT | QUAT Heat Trace |  | See Heat Trace | Inst, Cond & wire | Ex LPI Pnl | Quat Tk |  |  |  | 130 | 1C #10 | 30 | 0.75 | rgs | P-29 | 3
HT | Stor, CCA PW Stor H.T. |  | See Heat Trace | Inst, Cond & wire | Ex LPI Pnl | MEA Tk |  |  |  | 560 | 1C #10 | 180 | 0.75 | rgs | P-30 | 3
HT | MEA Stor Tk,NW PW Stor, Grd Wtr |  | See Heat Trace | Inst, Cond & wire | Ex LPI Pnl | MEA Tk |  |  |  | 560 | 1C #10 | 180 | 0.75 | rgs | P-31 | 3
| Outdoor Fix-1 |  | 175W Met Halide WP, stantion mt | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-32 | 3
| Outdoor Fix-2 |  | 175W Met Halide WP, stantion mt | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-33 | 3
| Outdoor Fix-3 |  | 175W Met Halide WP, stantion mt | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-34 | 3
| Outdoor Fix-4 |  | 175W Met Halide WP, stantion mt | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-35 | 3
| Outdoor Fix-5 |  | 175W Met Halide WP, stantion mt | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-36 | 3
| Inside Fix-1 |  | 400W Met Halide Lowbay | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-42
| Inside Fix-2 |  | 400 W met halide lamps only | Relamp Existing | Ex Circuits
| Inside Fix-2 |  | 400 W met halide lamps only | Relamp Existing | Ex Circuits
| Inside Fix-3 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-43
| Inside Fix-4 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-44
| Inside Fix-5 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-45
| Inside Fix-6 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-46
| Inside Fix-7 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-47
| Inside Fix-8 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-48
| Inside Fix-9 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-49
| Inside Fix-10 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-50
| Inside Fix-11 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-51
| Inside Fix-12 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-52
| Inside Fix-13 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-53
| Inside Fix-14 |  | 8 ft Fl, 2 tube Slimline w/chains | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-54
| Exit sign |  | Arrow | relocate, cond & wire | Ex Circuits | ex fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-55
| CR Fix |  | 2 lamp F40 | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-56
| CR- Air Cond |  | 120 Ckt/outlet | Inst, Cond & wire | Ex Circuits | New Outlet |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-56
| CR- Heat |  | 120 Ckt/outlet | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-56
| CR-computer |  | 120 Ckt/outlet | Inst, Cond & wire | Ex Circuits | New Fix |  |  |  | 150 | 1C#10 | 40 | 0.75 | emt | P-56
| PP-1 Boiler |  | 225A 42 pole 480/277V panel | Inst, Cond & wire | EX MDP in ER | PP-1 |  |  |  | 500 | 1C#4/0 | 160 | 2.5 | emt | P-37 | 5
| PP-1 Boiler |  |  |  | EX MDP in ER | PP-1 |  |  |  | 340 | 1C#2
| Boiler Pwr |  |  | Inst, Cond & wire | PP-1 | Blr |  |  |  | 200 | 1C#3 | 60 | 1.25 | emt | P-38 | 4
| Boiler Pwr |  |  |  | PP-1 | Blr |  |  |  | 70 | 1C#8
| Boiier FW |  |  | Inst, Cond & wire | PP-1 | BlrFW Pmp |  |  |  | 250 | 1C#4/0 | 60 | 0.75 | emt | P-39 | 4
| Boiier FW |  |  |  | PP-1 | Blr FW Pmp |  |  |  | 250 | 1C#4/0 | 60 | 0.75 | emt | P-40 | 4
| D&R-1 |  |  | Relocate Outside lights on moved wall | Ex Circuits |  |  |  |  | 300 | 1C#12 | 100 | 0.75 | emt |  | 3
| D&R-2 |  |  | Relocate Exit sign | Ex Circuits |  |  |  |  | 300 | 1C#12 | 100 | 0.75 | emt |  | 3
| D&R-3 |  |  | Relocate (3) 120V recept | Ex Circuits |  |  |  |  | 300 | 1C#12 | 100 | 0.75 | emt |  | 3

## conduit
Cond Runs | Unit MH | MH/100FT |  | Ft | Size | Type | unions | Straps | "T"s | hubs | 3/4X RE | LB | Ft Flex | Flex Bush | total mat unit
|  |  |  | 50 | 0.75 | emi | 3 | 5 |  |  |  | 1
|  |  |  | 100 | 0.75 | emt | 5 | 10 |  |  |  | 1
|  |  |  | 100 | 0.75 | emt | 5 | 10 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | emt | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 20 | 0.75 | EMT | 1 | 2 |  |  |  | 1
|  |  |  | 30 | 0.75 | emt | 2 | 3 |  |  |  | 1
|  |  |  | 30 | 0.75 | emt | 2 | 3 |  |  |  | 1
|  |  |  | 30 | 0.75 | emt | 2 | 3 |  |  |  | 1
|  |  |  | 30 | 0.75 | emt | 2 | 3 |  |  |  | 1
|  |  |  | 80 | 0.75 | emt | 4 | 8 | 1 |  |  | 1
|  |  |  | 100 | 0.75 | emt | 5 | 10 |  |  |  | 1
|  |  |  | 80 | 0.75 | emt | 4 | 8 |  |  |  | 1
|  |  |  | 80 | 0.75 | emt | 4 | 8 |  |  |  | 1
|  |  |  | 150 | 0.75 | emt | 8 | 15 | 2 |  |  | 1
|  |  |  | 150 | 0.75 | emt | 8 | 15 | 2 |  |  | 1
|  |  |  | 150 | 0.75 | emt | 8 | 15 | 2 |  |  | 1
|  |  |  | 150 | 0.75 | emt | 8 | 15 | 2 |  |  | 1
|  |  |  | 150 | 0.75 | emt | 8 | 15 | 2 |  |  | 1
|  |  |  | 80 | 0.75 | emt | 4 | 8 |  |  |  | 1
|  |  |  | 100 | 0.75 | emt | 5 | 10 | 2 |  |  | 1
|  |  |  | 100 | 0.75 | emt | 5 | 10 | 2 |  |  | 1
|  |  |  | 125 | 0.75 | emt | 6 | 12 | 3 |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 40 | 0.75 | emt | 2 | 4 |  |  |  | 1
|  |  |  | 60 | 0.75 | emt | 3 | 6 | 3 |  |  | 1
|  |  |  | 360 | 0.75 | emt | 18 | 36 | 3 |  |  | 1
77 | 384.6 | 8 | Totals | 3845 | 0.75 | emt | 197 | 384 | 24 | 0 | 0 | 77 | 0 | 0
| 17480.07 |  | Mat cost ea |  |  | 0
|  |  | Mat unit cost |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 60 | 1 | emt | 3 | 6 | 1 |  | 1 | 1 | 2 | 2
|  |  |  | 60 | 1 | EMT | 3 | 6 | 3 |  | 3 | 1 | 2 | 2
2 | 14 | 10 | Totals | 120 | 1 | EMT | 6 | 12 | 4 | 0 | 4 | 2 | 4 | 4
| 636.3 |  | Mat cost ea |  |  | 0
|  |  | Mat unit cost |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 60 | 1.25 | EMT | 3 | 6 | 7 |  | 7 | 1
|  |  |  | 80 | 1.25 | emt | 4 | 8 | 2 |  | 2 | 1
|  |  |  | 60 | 1.25 | emt | 3 | 6 |  |  |  | 1
3 | 25 | 11 | Totals | 200 | 1.25 | emt | 10 | 20 | 9 | 0 | 9 | 3 | 12 | 0
| 1136.25 |  | Mat cost ea |  |  | 0
|  |  | Mat unit cost |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 60 | 1.5 | EMT | 3 | 6 | 4 |  | 4 | 1
|  |  |  | 60 | 1.5 | EMT | 3 | 6 | 4 |  | 4 | 1
2 | 16.4 | 12 | Totals | 120 | 1.5 | EMT | 6 | 12 | 8 | 0 | 8 | 2 | 0 | 0
| 745.38 |  | Mat cost ea |  |  | 0
|  |  | Mat unit cost |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 60 | 2 | EMT | 3 | 6 | 5 |  | 5 | 1
|  |  |  | 60 | 2 | EMT | 3 | 6 | 6 |  | 6 | 1
|  |  |  | 80 | 2 | emt | 4 | 8 |  |  |  | 1
|  |  |  | 150 | 2 | emt | 7.5 | 15 |  |  |  | 2
4 | 53 | 14 | Totals | 350 | 2 | emt | 17.5 | 35 | 11 | 0 | 11 | 5 | 0 | 0
| 2408.85 |  | Mat cost ea |  |  | 0
|  |  | Mat unit cost |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 160 | 2.5 | emt | 8 | 16 |  |  |  | 2
1 | 29.8 | 18 | Totals | 160 | 2.5 | emt | 8 | 16 | 0 | 0 | 0 | 2 | 0 | 0
| 1354.41 |  | Mat cost ea |  |  | 0
|  |  | Mat unit cost |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 100 | 0.75 | rgs | 5 | 10 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 0.75 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 250 | 0.75 | rgs | 12.5 | 25 |  |  |  | 3 | 2 | 2
|  |  |  | 120 | 0.75 | rgs | 6 | 12 |  |  |  | 1 | 2 | 2
|  |  |  | 120 | 0.75 | rgs | 6 | 12 |  |  |  | 1 | 2 | 2
|  |  |  | 80 | 0.75 | rgs | 4 | 8 |  |  |  | 1 | 2 | 2
|  |  |  | 300 | 0.75 | rgs | 15 | 30 |  |  |  | 2 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 2 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 2 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 2 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 2 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 2 | 2 | 2
|  |  |  | 100 | 0.75 | rgs | 5 | 10 |  |  |  | 2 | 2 | 2
|  |  |  | 100 | 0.75 | rgs | 5 | 10 |  |  |  | 2 | 2 | 2
|  |  |  | 30 | 0.75 | rgs | 1.5 | 3 |  |  |  | 2 | 2 | 2
|  |  |  | 30 | 0.75 | rgs | 1.5 | 3 |  |  |  | 1 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 1 | 2 | 2
|  |  |  | 180 | 0.75 | rgs | 9 | 18 |  |  |  | 1 | 2 | 2
65 | 479 | 12 | Totals | 3450 | 0.75 | rgs |  | 345 | 0 | 138 | 0 | 76 | 130 | 130
| 21770.55 |  | Mat cost ea |  |  | 49.5 |  |  |  | 1.6 |  | 5.24
|  |  | Mat unit cost |  |  | 1707.75 | 0 | 0 | 0 | 220.8 | 0 | 398.24 | 0 | 0 | 2326.79
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 20 | 1 | rgs | 1 | 2 |  |  |  | 1 | 2 | 2
|  |  |  | 100 | 1 | rgs | 5 | 10 | 4 |  | 4 | 1
|  |  |  | 100 | 1 | rgs | 5 | 10 | 3 |  | 3 | 1
|  |  |  | 100 | 1 | rgs | 5 | 10 |  |  | 0 | 1
|  |  |  | 250 | 1 | rgs | 12.5 | 25 | 1 |  | 1 | 2
|  |  |  | 120 | 1 | rgs | 6 | 12 | 6 |  | 6 | 1
22 | 163.4 | 14 | Totals | 1010 | 1 | rgs |  | 101 | 14 | 28 | 14 | 23 | 34 | 34
| 7426.53 |  | Mat cost ea |  |  | 70 |  |  |  | 1.84 |  | 13.4
|  |  | Mat unit cost |  |  | 707 | 0 | 0 | 0 | 51.52 | 0 | 308.2 | 0 | 0 | 1066.72
|  |  |  | 150 | 1.25 | rgs | 7.5 | 15 | 5 |  | 5 | 2
|  |  |  | 250 | 1.25 | rgs | 12.5 | 25 | 4 |  | 4 | 2
2 | 62 | 15 | Totals | 400 | 1.25 | rgs |  | 40 | 9 | 6 | 9 | 4 | 0 | 0
| 2817.9 |  | Mat cost ea |  |  | 100 |  |  |  | 2.5 |  | 6.1
|  |  | Mat unit cost |  |  | 400 | 0 | 0 | 0 | 15 | 0 | 24.4 | 0 | 0 | 439.4
|  |  |  | 250 | 1.5 | rgs | 12.5 | 25 | 3 |  | 3 | 1
1 | 41 | 16 | Totals | 250 | 1.5 | rgs |  | 25 | 3 | 4 | 3 | 1 | 0 | 0
| 1863.45 |  | Mat cost ea |  |  | 111 |  |  |  | 2.76 |  | 6.1
|  |  | Mat unit cost |  |  | 277.5 | 0 | 0 | 0 | 11.04 | 0 | 6.1 | 0 | 0 | 294.64
|  |  |  | 150 | 2 | rgs | 7.5 | 15 | 6 |  | 6 | 1
|  |  |  | 150 | 2 | rgs | 7.5 | 15 | 4 |  | 4 | 1
|  |  |  | 300 | 2 | rgs | 15 | 30 | 5 |  | 5 | 3
|  |  |  | 300 | 2 | rgs | 15 | 30 | 4 |  | 4 | 3
4 | 166 | 18 | Totals | 900 | 2 | rgs | 45 | 90 | 19 | 10 | 19 | 8 | 0 | 0
| 7544.7 |  | Mat cost ea |  |  | 145 |  |  |  | 5 |  | 8.84
|  |  | Mat unit cost |  |  | 1305 | 0 | 0 | 0 | 50 | 0 | 70.72 | 0 | 0 | 1425.72
|  |  |  | 200 | 2.5 | rgs | 10 | 20 | 7 |  | 7 | 3
1 | 45 | 22 | Totals | 200 | 2.5 | rgs | 10 | 20 | 7 | 6 | 7 | 3 | 0 | 0
| 2045.25 |  | Mat cost ea |  |  | 160 |  |  |  | 6 |  | 15.3
|  |  | Mat unit cost |  |  | 320 | 0 | 0 | 0 | 36 | 0 | 45.9 | 0 | 0 | 401.9
|  |  |  | 30 | 3 | rgs | [5 empty] | 1
|  |  |  | 60 | 3 | rgs | [5 empty] | 1
2 | 23.6 | 24 | Totals | 90 | 3 | rgs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1072.62 |  | Mat cost ea |  |  | 185
|  |  | Mat unit cost |  |  | 166.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.5
Runs
186 | 1502.8 |  | Total MH
Add 1 MH/R | 186 | [9 empty] | Total Material incl below |  |  |  | 8181.67
| 76755.96 |  | Total conduit cost
[7 empty] | Other hardware |  |  | Qty | Des |  |  | $/100
[10 empty] | 500 | ft of P1000 Galv Strut |  |  | 88 | 440
[10 empty] | 600 | 3/4" Galv Strap & bolts |  |  | 33 | 198
[10 empty] | 200 | 1" Galv Strap & Blot |  |  | 48 | 96
[10 empty] | 100 | 1.5" Galv Strap & bolts |  |  | 55 | 55
[10 empty] | 50 | Eys 3/4 |  |  | 620 | 310
[10 empty] | 30 | Eys 1 |  |  | 760 | 228
[10 empty] | 20 | Eyes 1.5 |  |  | 1490 | 298
[10 empty] | 10 | Eyes 2 |  |  | 1600 | 160
[10 empty] | 1000 | ft of pull string |  |  |  | 25
[10 empty] | 200 | .5 close nipples |  |  |  | 250
[14 empty] | total | 2060
The acual individual runs are in hidden rows, only totals are shown to make an estimate UnHide all rows

## cable
| 130 | 1C#10
| 130 | 1C#10
| 560 | 1C#10
| 560 | 1C#10
| 110 | 1C#10
| 110 | 1C#10
| 110 | 1C#10
| 110 | 1C#10
| 130 | 1C#10
| 130 | 1C#10
| 290 | 1C#10
| 930 | 1C#10
| 290 | 1C#10
| 290 | 1C#10
| 460 | 1C#10
| 160 | 1C#10
| 160 | 1C#10
| 460 | 1C#10
| 460 | 1C#10
| 90 | 1C#10
| 190 | 1C#10
| 190 | 1C#10
| 190 | 1C#10
| 190 | 1C#10
| 190 | 1C#10
| 110 | 1C#10
| 110 | 1C#10
| 110 | 1C#10
| 110 | 1C#10
| 400 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10
| 150 | 1C#10 THHN
| cable footage | type | Cost per 100 ft | Unit cost | MH to install 100ft | unit MH | Labor sell
Totals | 10910 | 1C#10 THHN | 47.6 | 5193.16 | 0.75 | 81.825 | 3718.9462
| 90 | 1C#12
| 310 | 1C#12
| 90 | 1C#12
| 90 | 1C#12
| 160 | 1C#12
| 160 | 1C#12
| 900 | 1C#12 for D&R
| 160 | 1C#12
| 135 | 1C#12
Totals | 2095 | 1C#12 | 31 | 649.45 | 0.5 | 10.475 | 476.0888
| 340 | 1C#2
Totals | 340 | 1C#2 |  | 0 | 2 | 6.8 | 309.06
| 460 | 1C#2/0
Totals | 460 | 1C#2/0 | 680.02 | 3128.092 | 2.5 | 11.5 | 522.675
| 200 | 1C#3
Totals | 200 | 1C#3 | 290 | 580 | 1.5 | 3 | 136.35
| 160 | 1C#4
Totals | 160 | 1C#4 | 290 | 464 | 1.5 | 2.4 | 109.08
| 500 | 1C#4/0
| 250 | 1C#4/0
| 250 | 1C#4/0
Totals | 1000 | 1C#4/0 |  | 0 | 3 | 30 | 1363.5
| 460 | 1C#8
| 460 | 1C#8
| 290 | 1C#8
| 550 | 1C#8
| 550 | 1C#8
| 550 | 1C#8
| 550 | 1C#8
| 550 | 1C#8
| 350 | 1C#8
| 350 | 1C#8
| 350 | 1C#8
| 350 | 1C#8
| 70 | 1C#8
| 400 | 1C#8,
| 400 | 1C#8,
Totals | 6230 | 1C#8, |  | 0 | 1 | 62.3 | 2831.535
| 260 | 2C#16
| 260 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 510 | 2C#16
| 260 | 2C#16
| 260 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 270 | 2C#16
| 90 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 190 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 990 | 2C#16
| 550 | 2C#16
| 550 | 2C#16
| 550 | 2C#16
| 550 | 2C#16
| 110 | 2C#16
| 110 | 2C#16
| 220 | 2C#16
| 220 | 2C#16
| 220 | 2C#16
| 300 | 2C#16
| 300 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 100 | 2C#16
| 700 | 2C#16
| 700 | 2C#16
| 700 | 2C#16
| 700 | 2C#16
| 700 | 2C#16
| 700 | 2C#16
| 700 | 2C#16
Totals | 32890 | 2C#16 |  | 0 | 0.75 | 246.675 | 11211.3787
| 130 | 2C#16 shd
| 130 | 2C#16 shd
| 130 | 2C#16 shd
| 130 | 2C#16 shd
| 110 | 2C#16 shd
| 180 | 2C#16 shd
| 180 | 2C#16 shd
| 180 | 2C#16 shd
| 180 | 2C#16 shd
| 180 | 2C#16 shd
| 180 | 2C#16 shd
| 90 | 2C#16 shd
| 90 | 2C#16 shd
| 90 | 2C#16 shd
| 90 | 2C#16 shd
| 90 | 2C#16 shd
| 90 | 2C#16 shd
| 90 | 2C#16 shd
| 280 | 2C#16 shd
| 280 | 2C#16 shd
| 280 | 2C#16 shd
| 280 | 2C#16 shd
| 280 | 2C#16 shd Beldon 8760 or =
Totals | 3740 | 2C#16 shd Beldon 8760 or = | 130 | 4862 | 0.75 | 28.05 | 1274.8725
| 120 | 350MCM THHN
| 120 | 350MCM THHN
Totals | 240 | 350MCM THHN |  | 0 | 6 | 14.4 | 654.48
| 120 | 3C#12 THHN
| 110 | 3C#12 THHN
Totals | 230 | 3C#12 THHN |  | 0 | 0.75 | 1.725 | 78.4013
| 90 | 3C#16
| 90 | 3C#16
| 90 | 3C#16
| 90 | 3C#16
| 280 | 3C#16
| 280 | 3C#16
| 110 | 3C#16
Totals | 1030 | 3C#16 |  | 0 | 0.5 | 5.15 | 234.0675
| 90 | 3C#16 shd
| 90 | 3C#16 shd
| 280 | 3C#16 shd
Totals | 460 | 3C#16 shd |  | 0 | 0.5 | 2.3 | 104.535
| 220 | coax RG59/U
Totals | 460 | coax RG59/U |  | 0 | 0.5 | 2.3 | 104.535
|  | Totals |  | 14876.702 |  | 522.5 | 23747.625
| 904 | Wire Markers required | 45 | 406.8 | 1.5 | 13.56 | 616.302
| 452 | Stacons at device end | 33 | 149.16 | 2 | 9.04 | 410.868
Some rows are hidden contain individual runs, only total are shown
for making an estimate UNHIDE rowes

## hardware
| Summary from below |  | 0 | 6666.6 | 0 | 362 | 16452.9
QTY | Electrical Hardware & Air Tubing by CSC |  | cost | sell | MH Ea | Unit MH | Labor Sell | Labor Calc | 1st cl | 2nd cl | 3rd cl | helper
|  |  |  | 0 |  | 0 | 0 | 45.45 | 26.05 | 24.1 | 21.02 | 17.85
3 | Cast Alum Deep SG Box w/ duplex 115v recpt |  | 9 | 32.4 | 0.8 | 2.4 | 109.08 | 1 MH in calc is for 2 men, a journey man. A forman is factored in
5 | 175W Metal Halide WP lamp and fixture with stantion for outside mountingt |  | 30 | 180 | 3 | 15 | 681.75
1 | 2 lamp F40 |  | 55 | 66 | 1 | 1 | 45.45
1 | 225A 42 pole 480/277V panel |  | 355 | 426 | 6 | 6 | 272.7
5 | 20A SP 277vac GFCI Ckt Bkrs w/ panel |  | 35 | 210 | 0.7 | 3.5 | 159.075
2 | 277vac Fluorescent Fixture with lamps |  | 40 | 96 | 2 | 4 | 181.8
3 | 400 W met halide lamps only |  | 20 | 72 | 0.7 | 2.1 | 95.445
1 | 400W Met Halide Lowbay wall mounting lamp & fixture |  | 90 | 108 | 2 | 2 | 90.9
12 | 8 ft Fl, 2 tube Slimline Fluorescent Fixturesw/8' hanging chains |  | 45 | 648 | 1 | 12 | 545.4
25 | NEMA 4 Start/Stop PB-Sta with covered stop button |  |  | 0 | 0.7 | 17.5 | 795.375
6 | Non-fused local NEMA 4, HP Rated Disc switch | 1 hp | 26 | 187.2 | 0.7 | 4.2 | 190.89
4 | Non-fused local NEMA 4, HP Rated Disc switch | 2 hp | 30 | 144 | 0.7 | 2.8 | 127.26
3 | Non-fused local NEMA 4, HP Rated Disc switch | 5 hp | 32 | 115.2 | 0.7 | 2.1 | 95.445
4 | Non-fused local NEMA 4, HP Rated Disc switch | 10 hp | 38 | 182.4 | 0.7 | 2.8 | 127.26
6 | Non-fused local NEMA 4, HP Rated Disc switch | 15 hp | 38 | 273.6 | 0.7 | 4.2 | 190.89
1 | Non-fused local NEMA 4, HP Rated Disc switch | 20 hp | 45 | 54 | 0.7 | 0.7 | 31.815
1 | Non-fused local NEMA 4, HP Rated Disc switch | 100 hp | 85 | 102 | 0.7 | 0.7 | 31.815
1 | PP-1 Boiler |  | 145 | 174 | 4 | 4 | 181.8
1 | PP-1 Boiler |  | 145 | 174 | 4 | 4 | 181.8
1 | Boiler Pwr |  | 30 | 36 | 2 | 2 | 90.9
1 | Boiler Pwr |  | 30 | 36 | 2 | 2 | 90.9
1 | Boiier FW |  | 30 | 36 | 2 | 2 | 90.9
1 | Boiier FW |  | 30 | 36 | 2 | 2 | 90.9
1 | Contrl Room Telephone line |  | 100 | 120 | 4 | 4 | 181.8
3 | Control Room 120 V Wall recept |  | 30 | 108 | 2 | 6 | 272.7
12 | Transmitter mounting Brackets/floor stands |  | 125 | 1800 | 1 | 12 | 545.4
0
| Totals |  |  | 5416.8 |  | 121 | 5499.45
| Equipment by Owner installed by CSC |  |  |  | MH Ea | Unit MH | Labor Sell
| Motors to connect | HP
1 | CCA LO Pmp | 15 | 5 | 6 | 2 | 2 | 90.9
1 | QUAT Pmp | 2 | 5 | 6 | 1 | 1 | 45.45
1 | MW100 T Pmp | 15 | 5 | 6 | 2 | 2 | 90.9
1 | MW100 LO Pmp | 15 | 5 | 6 | 2 | 2 | 90.9
1 | CT Fan | 10 | 5 | 6 | 2 | 2 | 90.9
1 | CT Pmp | 10 | 5 | 6 | 2 | 2 | 90.9
1 | AF Tk Mix | 1.5 | 5 | 6 | 1 | 1 | 45.45
1 | AF-Add Pmp | 1.5 | 5 | 6 | 1 | 1 | 45.45
1 | Bag UnL RV | 1 | 5 | 6 | 1 | 1 | 45.45
1 | Reac Mixer | 15 | 5 | 6 | 2 | 2 | 90.9
1 | Reac Vac Pmp | 15 | 5 | 6 | 2 | 2 | 90.9
1 | Rac FR RV | 1 | 5 | 6 | 1 | 1 | 45.45
1 | Reac Pmp | 15 | 5 | 6 | 2 | 2 | 90.9
1 | Reac PD Blower | 100 | 30 | 36 | 5 | 5 | 227.25
1 | CO Bag UnL | 1 | 5 | 6 | 1 | 1 | 45.45
1 | PreHt Pmp | 10 | 5 | 6 | 2 | 2 | 90.9
1 | MEA Pmp | 10 | 5 | 6 | 2 | 2 | 90.9
1 | MEA Sump 1 | 1 | 5 | 6 | 1 | 1 | 45.45
1 | MEA Sump 2 | 1 | 5 | 6 | 1 | 1 | 45.45
1 | MW100 PW Pmp | 5 | 5 | 6 | 1 | 1 | 45.45
1 | CCA PW Pmp | 5 | 5 | 6 | 1 | 1 | 45.45
1 | FF Tk Pmp | 20 | 10 | 12 | 2 | 2 | 90.9
1 | Pre-Coat Agit | 0.5 | 5 | 6 | 1 | 1 | 45.45
1 | FF Tk Agit | 3 | 5 | 6 | 1 | 1 | 45.45
1 | Exhaust Fan | 2 | 5 | 6 | 1 | 1 | 45.45
| Totals |  |  | 186 |  | 40 | 1818
| Starters to wire |  |  |  | MH Ea | Unit MH | Labor Sell
1 | CCA LO Pmp | 15 |  |  | 3 | 3 | 136.35
1 | QUAT Pmp | 2 |  |  | 2 | 2 | 90.9
1 | MW100 T Pmp | 15 |  |  | 3 | 3 | 136.35
1 | MW100 LO Pmp | 15 |  |  | 3 | 3 | 136.35
1 | CT Fan | 10 |  |  | 3 | 3 | 136.35
1 | CT Pmp | 10 |  |  | 3 | 3 | 136.35
1 | AF Tk Mix | 1.5 |  |  | 2 | 2 | 90.9
1 | AF-Add Pmp | 1.5 |  |  | 2 | 2 | 90.9
1 | Bag UnL RV | 1 |  |  | 2 | 2 | 90.9
1 | Reac Mixer | 15 |  |  | 3 | 3 | 136.35
1 | Reac Vac Pmp | 15 |  |  | 3 | 3 | 136.35
1 | Rac FR RV | 1 |  |  | 1 | 1 | 45.45
1 | Reac Pmp | 15 |  |  | 3 | 3 | 136.35
1 | Reac PD Blower | 100 |  |  | 5 | 5 | 227.25
1 | CO Bag UnL | 1 |  |  | 2 | 2 | 90.9
1 | PreHt Pmp | 10 |  |  | 3 | 3 | 136.35
1 | MEA Pmp | 10 |  |  | 3 | 3 | 136.35
1 | MEA Sump 1 | 1 |  |  | 2 | 2 | 90.9
1 | MEA Sump 2 | 1 |  |  | 2 | 2 | 90.9
1 | MW100 PW Pmp | 5 |  |  | 2 | 2 | 90.9
1 | CCA PW Pmp | 5 |  |  | 2 | 2 | 90.9
1 | FF Tk Pmp | 20 |  |  | 3 | 3 | 136.35
1 | Pre-Coat Agit | 0.5 |  |  | 2 | 2 | 90.9
1 | FF Tk Agit | 3 |  |  | 2 | 2 | 90.9
1 | Exhaust Fan | 2 |  |  | 2 | 2 | 90.9
| Totals |  |  | 0 |  | 63 | 2863.35
| Instruments |  |  |  | MH Ea | Unit MH | Labor Sell
1 | PLC-1 |  | 150 | 180 | 8 | 8 | 363.6
1 | OWS-1 |  | 50 | 60 | 2 | 2 | 90.9
1 | OWS-1 |  |  | 0 | 2 | 2 | 90.9
1 | FCV-R1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FT-FP-FILT |  | 5 | 6 | 1 | 1 | 45.45
1 | FT-FP-FILT |  | 2 | 2.4 | 1 | 1 | 45.45
1 | FT-MEA-PMP |  | 2 | 2.4 | 1 | 1 | 45.45
1 | FT-MEA-PMP |  | 2 | 2.4 | 1 | 1 | 45.45
1 | FT-P/ST PW |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-P/ST PW |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-QUAT |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-R1 |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-R1 |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-R2 |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-R2 |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-R3 |  | 2 | 2 | 1 | 1 | 45.45
1 | FT-R3 |  | 2 | 2 | 1 | 1 | 45.45
1 | FV-AF |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-CCA20-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-CCA-20-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-CCA26-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-CCA26-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-MEA-1-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-MEA-1-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-MEA-1-3 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-MEA-2-4 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-MEA-2-5 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-MEA-2-6 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-A-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-A-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-B-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-B-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-C-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-C-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-D-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-D-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-E-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-NW100-E-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-P/ST-10 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-P/ST-11 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-P/ST-7 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-P/ST-8 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-P/ST-9 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-QUAT-1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-QUAT-2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-QUAT-3 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R1 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R3 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R4 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R5 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R6 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R7 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | FV-R8 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | KV-Bag UnL |  | 2 | 2.4 | 2 | 2 | 90.9
1 | LS-REAC |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-CCA20 |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-CCA26 |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-FF TK |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-MEA-1-2 |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-MEA-2-3 |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-NW100-A |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-NW100-B |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-NW100-C |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-NW100-D |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-NW100-E |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-P/ST-1 |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-QUAT |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-REAC |  | 2 | 2.4 | 1 | 1 | 45.45
1 | LT-REAC |  | 2 | 2.4 | 1 | 1 | 45.45
1 | MCC-1 |  | 120 | 144 | 8 | 8 | 363.6
1 | TCV-R2 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | TCV-R3 |  | 12 | 14.4 | 2 | 2 | 90.9
1 | TE-HEATEXC |  | 5 | 3 | 1 | 1 | 45.45
1 | TE-P/ST |  | 5 | 3 | 1 | 1 | 45.45
1 | TE-REAC |  | 5 | 3 | 1 | 1 | 45.45
1 | VS-QUAT |  | 15 | 18 | 3 | 3 | 136.35
1 | WE-NW100-S |  | 6 | 7.2 | 2 | 2 | 90.9
| Totals |  |  | 1063.8 |  | 138 | 6272.1

## summary
Osmose Salt Treating Plant
Rock Hill, SC | Men | Fore | Duration in weeks |  | Total Proposal |  | 204696.7268
Job duration based on 40 hrs/ wk | 8 | 1 | 7.83
Checkout 2 weeks | 2 |  | 2
|  |  | Material | Overhd | MH | Labor sell
Checkout (2 Men, 2 weeks) |  |  |  | 450 | 160 | 7272
Grounding Summary |  |  | 1473.8 |  | 79.9 | 3631.455
Heat Tracing Summary |  |  | 3317.04 |  | 38.4 | 1745.28
Conduit Summary |  |  | 8181.67 |  | 1502.8 | 76755.96
Cable Summary |  |  | 14876.702 |  | 522.5 | 23747.625
Hardware & Instr summary from below |  |  | 6666.6 |  | 362 | 16452.9
Subtotal proposal price |  |  | 34515.812 |  | 2505.6 | 129605.22 | 166626.632
trucks & tools |  |  |  | 3523.5 |  |  | 3523.5
Storage & Equip Rentals |  |  |  | 8331.3316 |  |  | 8331.3316
foreman |  |  |  |  | 313.2 | 9552.6 | 9552.6
Contingency |  |  |  | 16662.6632 |  |  | 16662.6632